## Home
Topic | Identifying All critical Quality parameter of Purified Water generation and distribution
1 | Critical Quality Parameter
2 | Fish-Bone on Failure Mode analysis of Purified Water generation and distribution
3 | FMEA of Purified water generation and distribution system
Visit : https://pres.net.in

## Parameter
Failure Mode analysis of Purified Water generation and distribution
Material | Machine | Man | Method | Measurement | Mother Earth | Lab Control | Sanitization | Documentation | HMI/IPC/PLC Controls
Chemicals usages | Recirculation Pump with VFD | Training | Roughness verification | Calibration | Area cleaning | Solution preparation/dilution | Effectiveness | Line Modification | Auto dumping interlock
NaoCl | Distribution Pump | Hygiene | Joints/Boroscopy | TOC | Seasonal variation | Labelling and identification | Frequency | Spare maintenance | Pump change over
HCl | Sanitary pump | Testing | Hydro Test | Conductivity | Bio film formation | Hold Time of sample | Time | Preventive maintenance | Recirculation
SMBS | Spray Ball 360 deg | Incident reporting | Slope verification | pH | Power failure | Sample storage/handling | Hot water sanitization | Change control procedure | Line Filter pressure monitor
Anti scaling | Storage tank | Breakdown handling | Passivation | Flow meter | Testing lab qualification | Analyst error | Ozone sanitization | Breakdown metenance | Online monitoring
Feed water source/quality | Leakages | Analyst Qualification | Velocity | Temperature Transmitter | Tank inner jacket rupture | Testing delay | Back wash of UF | Trending | Audit trial
Compressed Air | Corrosion | Handling of sample | Turbulent flow | Ozone Sensor |  | Sampling kit preparation | Loop sanitization and draining | Report generation & review | Password control
Gasket GMP grade | Ozone generator | Chemical testing | Reynolds Number | UV intensity/running hr. |  |  |  | Routine monitoring | Recipe management
Bursting Disc and PLC control | Distribution piping | Microbial testing | Tank coverage study | ORP sensor |  |  |  | Alert and action level | Data backup
Contact part MOC 316L | RO membrane replacement | In adequate training | Dranablity Study | Pressure gauges |  |  |  |  | Software backup
Zero dead leg valve user point |  |  | Hold Time study | Dosing Pump |  |  |  |  | Time & Date setting
Dead leg not more than 1.5D |  |  | Sample Analysis | Level transmitter |  |  |  |  | Networking
Silicon tubing/leachablity |  |  | Labelling and identification | Dosing rate |  |  |  |  | Faulty cable connection
Air filter Maintenance |  |  | QC Release | Sensor Malfunctioning |  |  |  |  | Alarm and interlock
Filter jacket temperature |  |  | Solution preparation/dilution | [5 empty] | Quality logics control
Integrity |  |  | Hold Time study | [5 empty] | UF
Replacement |  |  | Approved Vendor source | [5 empty] | High pressure
Damage/rupture |  |  | Sample storage | [5 empty] | Low pressure
Integrity |  |  | Analyst error | [5 empty] | RO
|  |  | Sampling kit preparation | [5 empty] | High Chlorine/ORP
|  |  | Testing delay/ storage condition | [5 empty] | High conductivity
EDI
High conductivity
Return
High conductivity
High TOC
Temperature high
Ozone sensor
UV
Ozone destruction

## Fishbone
Fish-Bone on Failure Mode analysis of Purified Water generation and distribution
[26 empty] | Return |  | Temperature high
High TOC
[24 empty] | Ozone sensor |  | High conductivity
Level transmitter
[11 empty] | Dosing Pump | [14 empty] | UF | High pressure
[11 empty] | Pressure gauges | [14 empty] | Low pressure
[11 empty] | ORP sensor |  |  | HMI/IPC/PLC Controls
[11 empty] | UV intensity/running hr. |  |  |  | Auto dumping interlock | [12 empty] | High conductivity
[11 empty] | Ozone Sensor |  |  |  |  | Pump change over | [9 empty] | RO | High Chlorine/ORP
[11 empty] | Temperature Transmitter | [5 empty] | Recirculation
| Method | [9 empty] | Flow meter |  |  |  | Time & Date setting |  |  | Line Filter pressure monitor
|  | Hold Time study | [8 empty] | pH | [7 empty] | Online monitoring
|  |  | Dranablity Study | [7 empty] | Conductivity |  |  |  |  | Documentation |  |  |  | Audit trial | [5 empty] | EDI | High conductivity
| Sample Analysis |  |  | Tank coverage study | [6 empty] | TOC | [5 empty] | Line Modification |  |  |  | Password control
[5 empty] | Reynolds Number |  |  |  | Measurement |  |  |  |  | Sanitization |  |  |  | Spare maintenance |  |  |  | Recipe management
|  | Labelling and identification |  |  |  | Turbulent flow |  |  |  |  | Calibration |  |  |  | Loop sanitization and draining |  |  |  | Preventive maintenance |  |  |  | Data backup |  |  | UV | Ozone destruction
|  | QC Release |  |  |  |  | Velocity |  |  |  |  | Dosing rate |  |  |  | Back wash of UF |  |  |  | Change control procedure |  |  |  | Software backup
|  | Solution preparation/dilution | [5 empty] | Passivation |  |  |  |  | Sensor Malfunctioning |  |  |  | Ozone sanitization |  |  |  | Breakdown metenance |  |  |  | Quality logics control
|  | Hold Time study | [6 empty] | Slope verification | [8 empty] | Hot water sanitization |  |  |  | Trending |  |  |  | Networking
|  | Approved Vendor source | [7 empty] | Hydro Test | [8 empty] | Time |  |  |  | Report generation & review |  |  |  | Faulty cable connection
|  | Sample storage | [8 empty] | Joints/Boroscopy | [8 empty] | Frequency |  |  |  | Routine monitoring |  |  |  | Alarm and interlock
|  | Analyst error | [9 empty] | Roughness verification | [8 empty] | Effectiveness |  |  |  | Alert and action level
Sampling kit preparation
|  | Testing delay/ storage condition | [9 empty] | RO membrane replacement |  |  |  | Training |  |  | Sampling kit preparation |  |  |  | Area cleaning |  |  |  |  | Chemicals usages
[11 empty] | Distribution piping |  |  |  | Hygiene |  |  | Testing delay |  |  |  | Seasonal variation
[10 empty] | Ozone generator |  |  |  | Testing |  |  | Analyst error |  |  |  | Bio film formation |  |  |  |  | Feed water source/quality |  |  | NaCl
[9 empty] | Corrosion |  |  |  | Incident reporting |  |  | Sample storage/handling |  |  |  | Power failure |  |  |  |  | Compressed Air |  |  |  | NaoCl
[8 empty] | Leakages |  |  |  | Breakdown handling |  |  | Hold Time of sample |  |  |  | Testing lab qualification |  |  |  |  | Gasket GMP grade |  |  |  |  | HCl
[7 empty] | Storage tank |  |  |  | Analyst Qualification |  |  | Labelling and identification |  |  |  | Tank inner jacket rupture |  |  |  |  | Gasket GMP grade | [5 empty] | SMBS
[6 empty] | Spray Ball 360 deg |  |  |  | Handling of sample |  |  | Solution preparation/dilution | [8 empty] | Bursting Disc and PLC control | [6 empty] | Anti scaling
[5 empty] | Sanitary pump |  |  |  | Chemical testing |  |  | Lab Control | [8 empty] | Bursting Disc and PLC control
|  |  |  | Distribution Pump |  |  |  | Microbial testing | [6 empty] | Mother Earth |  |  |  |  | Contact part MOC 316L
|  |  | Recirculation Pump with VFD |  |  |  | In adequate training | [11 empty] | Zero dead leg valve user point
|  | Machine |  |  |  | Man | [11 empty] | Dead leg not more than 1.5D
Silicon tubing/leachablity
Air filter Maintenance
[15 empty] | Material |  | Filter jacket temperature
Integrity
Replacement
Damage/rupture
Integrity
Failure Mode analysis of Purified Water generation and distribution

## FMEA
Risk Evaluation
System | Sub system/Item/ stage/Function | Failure modes | Potential effects of failure | Severity [S] | Mechanism of failure | Probability of occurrence [P] | Control | Detection [D] | RPN
NaOH Dosing Unit | NaOH dosing pump NaOH solution tank pH sensor | Dissolved gases (CO2) not removed through RO membrane | pH and Conductivity will not maintain | Low | It will pass through RO membrane | Low | 1. Gaseous CO2 will convert to dissolved ionic form by NaOH and further will removed by RO. 2. PLC control NaOH Dosing Unit is provided. | Medium | Low
Filtration | Cartridge Filter | Undissolved particle will pass through RO | RO membrane may damage | Low | If filter damage it will not able to retain the undissolved particles | Low | 1. Pressure gauge provided on the filter and out let to verify the pressure differential . | Medium | Low
Osmotron | Reverse Osmosis System | RO membrane could not be sanitized | permeate may be contaminated with time. | Low | If not sanitized with defined frequency | Low | 1. Hot water sanitization provision considered for RO membrane sanitization | Medium | Low
Osmotron | EDI (Electro deionisation) Module | High conductivity | Loss of time and generated water | Low | System will drain High conductivity water | Low | 1. Conductivity shall be monitored and recorded at downstream of EDI. | Medium | Low
Storage tank for Purified water | Level Transmitter | Water Level will not monitor/maintained | Water level will be low/high | Low | If system not installed Level transmitter | Low | 1. Level Transmitter considered as part of design to monitor level in the PW tank. 2. Tank will be provided with low level sensor to create alarm and stop supply water. 3. Tank will be provided with control system for sensing high level of water in tank and it will stop the supply of water in the tank. | Medium | Low
Storage tank for Purified water | Vent filter (0.2 μ hydrophobic) | Venting is not available Water may get contamination with viable and non viable particle | Microbial contamination | Low | 1. Storage tanks required venting to compensate for the dynamics of changing water levels. 2. If integrity of filter failed or choked | Low | 1. Sanitary vent filter (0.2 μ hydrophobic) considered with heat tracing housing. 2. Temperature transmitter is considered to monitor the vent filter jacket temperature. 2. Periodic filter integrity to be per formed as per procedure. | Medium | Low
Storage tank for Purified water | Dynamic Spray Balls | Tank internal surface not wet with water during normal operation, chemical and/or thermal sanitization. | Proliferation of microbiological organisms | Low | 1. If the spray balls are not able to wet entire tank including headspace | Low | 1. Dynamic spray balls considered to ensure that the entire tank surface including headspace is wetted with 360 Deg Rotation 2. Riboflavin tests to be performed to verify the spray coverage inside the vessel. | Medium | Low
Storage tank for Purified water | Tank drain valve | stagnancy of water | Microbial contamination | Low | If 100% drainage not happened through drain valve | Low | 1. Slope towards drain considered in vessel design 2. Drainablity study to considered during qualification. | Medium | Low
Storage tank for Purified water | Rupture disc | Tank will be under- and over-pressurization | Vessel can be damage | Low | Pressure-relief valves and bursting discs not considered | Low | 1. Rupture discs are provided on storage vessels to protect them from under- and over-pressurization 2. Rupture disks equipped with a rupture alarm device to safeguard for the mechanical integrity of the tank. 3. Compound pressure indicator considered for monitoring of tank pressure. | Medium | Low
Storage tank for Purified water | Temperature transmitter | Temperature probe malfunctioning | During sanitization temperature will not maintained | Low | Temperature probe if not calibrated | Low | 1. Temperature sensor PT100, RTD Sensor , Range-0 to 150°C considered 2. Periodic calibration to be considered as per the schedule | Medium | Low
Storage tank for Purified water | Tank does not have sanitary construction | Direct contact parts are not GMP grade | Chance for getting microbial contamination | Low | If the MOC of contact part are not GMP grade | Low | 1. Tank is made of SS316 L and tank is provided with steam jacket for heating of water required for sanitization. 2. Direct contact surface (tank, pipe, valve, spray ball, sensors) shall be made of SS316 L ( surface finish 0.3 m RA) or suitable elastomer e.g. PTFE, silicone etc. 3. All pipe connection shall be sanitary triclover type. | Medium | Low
Purified water distribution loop | Two No's of Pump with variable frequency drive (VFD) Flow transmitter | Velocity will not maintain Flow rate can not be monitor | Chance of proliferation of microbiological organisms and formation of biofilms | Low | 1. Pump malfunctioning 2. Lower velocity in distribution loop | Low | 1.Pump will maintenance of continuous turbulent flow circulation within water distribution systems 2. Centrifugal pumps for loop water re-circulation with VFD to maintain velocity in the line. 3. Variable frequency drive (VFD) to maintain return line velocity minimum 1.2 m/sec (4 f/sec). 4. Reynolds number verification to be performed as part of qualification to ensure the tabulate flow | Medium | Low
Purified water distribution loop | Online conductivity meter TOC analyser | Conductivity and TOC will be high in PW | Chance for getting microbial contamination | Low | 1. Improper installation 2. Uncalibrated instrument | Low | 1. Installation verification to be considered during qualification for conductivity and TOC analyser 2. Periodic calibration to be performed as per procedure | Medium | Low
Purified water distribution loop | Mechanical finish and MOC | 1. GMP grade material not used 2. Good engineering practices not followed | Chance for getting microbial contamination | Low | 1. Inadequate internal finish 2. Improper piping joints 3. Inadequate flanges, unions and valves | Low | 1. Internal material surface roughness of not greater than 0.8 micrometre (Ra). Electro-polishing improves the resistance of the stainless-steel material to surface corrosion. 2. Automatic Orbital welding consider for piping joints and 10 % joints are considered for quality inspection. 3. Hydro test to be considered for all PW distribution loops to test the for strength and leaks of piping. 4. Where flanges, unions or valves are used they are hygienic or sanitary design. 5. User point are considered with zero dead leg valve. | Medium | Low
Purified water distribution loop | Slope | Water stagnant in the loop | Chance for getting microbial contamination | Low | Improper slope of distribution loop | Low | 1. Slope of the distribution pipe line considered not less than 1:100 , so that the system can be completely drained. | Medium | Low
Purified water distribution loop | Passivation | Loops are not cleaned properly after installation | Chance for getting microbial contamination | Low | Passivation not performed | Low | 1. System shall be passivized after initial installation or after significant modification. After passivation system shall be cleaned. | Medium | Low
Sanitization | Purified water storage and distribution | Improper Sanitization | Chance for getting microbial contamination | Low | 1. If the sanitization is not effective 2. Frequency of sanitization not establish 3. Alternate sanitization procedure not available | Low | 1. PW loop is integrated with an automatic ozone sanitization & hot water sanitization process with the help of heating tank water by supplying steam to the tank jacket. 2. The temperature of the hot water in the PW tank and the distribution loop shall be monitored during sanitization cycle. 3. Frequency of sanitization to be established during performance qualification. | Medium | Low
System Controls and operational logics | Online monitoring and control logic | Not able to control and monitor online process data | System failure not able to recognize | Low | 1. Improper installation 2. If the system integration not qualified/verified | Low | 1. Online instruments like conductivity, TOC, temperature, flow rate, and pressure will facilitate improved operational control of the attributes and parameters and for process release. 2. Installation verification of all measurable devices to be performed during qualification 3. Control logics and system integration to be verified during operational qualification | Medium | Low
System Controls and operational logics | IPC / HMI/ PLC | 1. System allows the access to unauthorized user 2. Unauthorized use of the system and application software Wrong user profiles / privileges assignment 3. Wrong use of the system and application software 4. Same username / password assigned to multiple users 5. Wrong use of the system and application software and incorrect workflow traceability 6. Access to the application and to the Operational system without password 7. Unauthorized use of the system and application software 8. The system allows to change the date and time of the workstation The date and time reliability of the system results is compromised | System security failure | Low | Unavailability of different level of user privileges Improper assignment of user privileges | Low | A. Password Management : 1. Password is required to access the system 2. Different level of authorization is provided based on the operation Password length considered more than or equal to 6 character to strengthen the password 2. Password maximum age is consider for expiration of current password 3. Password history will prevent to select previous to select the old system password 4. Inactive time lockout duration will ensure the auto lock out of the system to prevent the unauthorized access in case of system is unattended 5. Unsuccessful attempt of more than 3 time will block the particular user authorization. B. User management : 1. The system shall have minimum 4 Access levels (Operator, Supervisor, Engineer and administrator). 2. Provision to create individual users. 3. Provision to create minimum two numbers of administrators. 4.Date and time change option shall be available only for administrator. 5. Operator shall have the privileges only to operate the equipment. | Medium | Low
System Controls and operational logics | IPC / HMI/ PLC | 1. The system does not allow to obtain correct and complete copies of data 2. Copies of GxP relevant data cannot be submitted in an appropriate format to the authorities 3. Data can be corrupted and falsified, with no trace Original data loss 4. Backup & Restore activities are not in place 5. Data loss | Data Integrity | Low | 1. Unavailability of data protection, back up and restoration procedure | Low | 1. System data transfer and archival is restricted to admin level 2. Software shall be provided by the OEM (Original Equipment Manufacturer) with current version and date. 3. GMP relevant data shall be available in non editable readable format. E.g. PDF | Medium | Low
System Controls and operational logics | IPC / HMI/ PLC | 1. The system audit trail does not record all required information related to performed changes | Data Traceability | Low | 1. Unavailability of Audit Trial | Low | 1. Audit trial provision available in the system. | Medium | Low
System Controls and operational logics | IPC / HMI/ PLC | The system does not automatically manage system operations according to recipe steps and process parameters, Process not correctly executed | Failure in Process/recipe Management | Low | 1. Unavailability of recipe management | Low | 1. System shall be run with configured recipe. 2. Any changes to the qualified recipe shall be performed based on the approved change request by System administrator. | Medium | Low
System Controls and operational logics | IPC / HMI/ PLC | The monitored process parameters are not correctly displayed Unfeasibility to record/monitor the process parameters values The system does not save monitored process parameters values Loss of monitored data related to process parameters | Failure in Critical Process Parameters Monitoring and Trends | Low | 1. System controls are not establish | Low | 1. Input output are considered as part of qualification program. 2. Safety interlocks and alarm shall be schemulate as a part of qualification. 3. System was provided with 240 GB hard drive for storage of process data. 4. Online / Offline data back up provision of process data has considered. | Medium | Low
Note on A1: Use shortcut key Ctrl+Shift+S to append a new sub system/item/stage/function